|  |  |
| --- | --- |
| Reason for Issue | Date |
| ***Building Permit Response 1***  (Building Permit #: CN-21-0056) | February 11, 2021 |
| Project Information | NORR Project No. |
| **New Shell Building - CFT Plaza**  **210 Malcolm Drive,**  **Westminster, MD** | JCDT19035100 |
|  |  |

### Intent

This **TRANSMITTAL** is issued to provide new and/or updated project documents.

### Drawings

The following DRAWINGS accompany and form a part of this **TRANSMITTAL**.

#### CIVIL

*Revised Drawings: G-1, C-1, L-1*

#### ARCHITECTURAL

*Revised Drawings: G 0.1, A 1.0, A 1.1, A 1.2, A 1.3, A 4.1, A 4.2, A 4.3, A 4.4, A 5.1, A 5.2,*

*A 6.1*

*STRUCTURAL*

*Revised Drawings: S-200 S-201*

*MECHANICAL*

*Revised Drawing: M1.1*

*PLUMBING*

*Revised Drawing: P1.0, P1.1*

*ELECTRICAL*

*Revised Drawing: E0.1, E1.1*

#### CIVIL DRAWING REVISIONS

* + - * 1. Dwg No G-1

Added accessibility compliance note.

* + - * 1. Dwg No C-1

Revised ramp at access path across drive-thru to ensure 5’-0” clear at top of ramp.

* + - * 1. Dwg No L-1

Updated location of plantings at rear of building to match revised sidewalk layout.

#### ARCHITECTURAL DRAWING REVISIONS

* + - * 1. Dwg No G 0.1

Updated Sheet Index to match current issuance (Permit Response 1), per clarification with drawing set.

Removed Fire Area B Occupant Load, deferred count to future tenant fit outs.

Updated parking count per civil revisions.

* + - * 1. Dwg. No. A 1.0

Revised background to show compliant landing width at top of ramp.

* + - * 1. Dwg. No. A 1.1

Revised background to show compliant landing width at top of ramp.

Updated door schedule notes per review comments.

Added note to 2 hour wall per review comments.

* + - * 1. Dwg No A 1.2

Added note regarding overlapping roof insulation seams per plan review.

* + - * 1. Dwg No A 1.3

Revised background to show compliant width at top of ramp.

* + - * 1. Dwg No A 4.1

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 4.2

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 4.3

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 4.4

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 5.1

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 5.2

Updated edge of slab detail to show R-10 insulation to top of slab.

* + - * 1. Dwg No. A 6.1

Updated door schedule notes per review comments.

Updated U and SHGC values required to correspond to comcheck values.

#### STRUCTURAL DRAWING REVISIONS

* + - * 1. Dwg. No. S-200

Revised in sections 2, 4, 6, 7, 8, 10 and 19, the detail of the slab on grade insulation to comply with IECC Section C402.2.4.

* + - * 1. Dwg. No. S-201

Revised in sections 3, 9, 11, 13, 13, 15 and 20, the detail of the slab on grade insulation to comply with IECC Section C402.2.4.

* + - 1. *MECHANICAL DRAWING REVISIONS*
         1. Dwg. No. M1.1

Clarified storm riser locations.

* + - 1. *PLUMBING DRAWING REVISIONS*
         1. Dwg. No. P1.0

Clarified invert elevations.

Clarified plumbing work shall comply with 2018 International Plumbing Code and Gas work shall comply with 2018 International Fuel Gas Code and NFPA 58 2017 for L.P.

* + - * 1. Dwg. No. P1.1

Clarified plumbing work shall comply with 2018 International Plumbing Code and Gas work shall comply with 2018 International Fuel Gas Code and NFPA 58 2017 for L.P.

* + - 1. *ELECTRICAL DRAWING REVISIONS*
         1. Dwg. No. E0.1

Added short circuit calculation to riser diagram.

Removed extraneous disconnects to comply with code disconnect requirement; T2, T3, T4 panels to be served from meter stack.

* + - * 1. Dwg. No. E1.1

Added switch ahead of tenant signage as a disconnecting means.